## Slide 1: Electric
Dave Soltys, Supervisor
Damage Prevention

## Slide 2: High Voltage Electricity Working around it safely

## Slide 3: Purpose of this Presentation
Raise Awareness
Explain Hazards of
Working with Electricity
Possible Solutions to
Hazards

## Slide 4: High Voltage Proximity Act
Voltage Level (Phase to Phase | 50kV & below | 115kV | 230kV | 345kV
Minimum distance in any direction between men or equipment to energized conductors | 10 ft | 15 ft | 17 ft | 20 ft

## Slide 5
13kV
Primary
2.4kV – 5kV
Primary & Street Ltg.
(up to 6k volts)
120V & 240V
Secondary
23kV – 46kV
Transmission
Notes: Here’s an example of the different voltages on our poles. The coating is not considered insulation (like an extension cord), it is to protect the metal conductor from the elements. Below our stuff is telephone and CATV.

## Slide 6: Typical Insulators & Method of Mounting on Poles
Multi-Skirt
Bell Shape
TRANSMISSION POST
INSULATOR
23,000 - 45,000 volts
PRIMARY
INSULATOR
13,200 volts
PRIMARY
INSULATOR
4,000 - 5,000 volts
Notes: Example of insulators used for different voltages

## Slide 7: Overhead Wire Touch Potential
10 Foot Minimum Clearance around all Electric Lines.
Be aware of your surroundings.
Notes: 2 ways in which workers are exposed to electric hazards are step potential and touch potential…..
Touch potential is when hazardous voltage goes to ground through the body. Hand to hand, hand to feet etc.

## Slide 8
They will energize any conductor they contact.
Survey the area closely.
Potential Conductors include: fences, gutters, antennas, railroad tracks, & aluminum siding.
All Downed Wires Must Be Considered
ENERGIZED & DEADLY !

## Slide 9
The Ground May Be Energized
Notes: Step potential is like the ripples in a pond. As energy moves away from the source the potential weakens. When a person steps away from a downed line the potential at one foot may be greater than the other foot and the electricity goes through the body if it has less resistance than the ground. Our employees are required to wear electric hazard (EH) rated work boots to minimize step potential. ( This is why it is recommended that if you are in an energized vehicle or piece of equipment you stay inside. If there is a greater hazard associated with staying inside i.e. fire, jump from the running board and land with both feet together as far away as possible.)

## Slide 10: Underground Electric Facilities
  Duct Banks w/ multiple conduit (concrete/clay)
  Conduit (Steel and Plastic)
  Direct Buried Cables
  Man Holes or Vaults

## Slide 11: Survey your surroundings BEFORE you dig
Look For:
Riser Poles/Pole Drops
Underground Vaults/Manholes/Handholes
Pad mounted transformers/Switches
Notes: Learn to read work area for clues to underground facilities…here is a riser pole

## Slide 13
High Tension Lines
aka Electric Transmission
Electric Manholes

## Slide 14
Riser drops
Notes: Here’s a riser pole feeding a pad mounted transformer…(what’s up with all the sneakers on our lines??)

## Slide 15: How many drops do you see?

## Slide 16: Underground Vaults/Manholes
Notes: Vaults/Manholes are primarily found in cities and house equipment and cable systems for the underground network.

## Slide 17
Substations

## Slide 18: Substations

## Slide 19: Pad Mount Transformers/Switches
Notes: Notice mark out 2’ around equipment to protect ground grid

## Slide 20: Transformers & Handholes

## Slide 21
Transformers
& Handholes

## Slide 22
Notes: Picture on left is from the street in, notice the bushes behind the fire Hydrant. Picture on the right is what’s behind the bushes.

## Slide 23: Private Electric

## Slide 24
Private Electric

## Slide 25: Electric Damage

## Slide 26: Effects of Electricity On the Body
Varies from no lasting affect to sever burns and fatalities
Remember, if the circuit is not:
De-energized
Locked/tagged out
Tested and grounded
IT’S NOT DEAD
Notes: If any employee experiences any electrical contact, they should be examined by a Dr immediately. Entry and exit wounds could appear very small but do severe damage to internal organs over time

## Slide 27: Questions?