## Slide 1
Propane/Air & Natural Gas Presentation

## Slide 2: Properties of Natural Gas and Propane
Natural Gas –
  Fossil fuel, Colorless, Odorless
    Odorant added for Identifiable Smell
  Non-toxic, Non-corrosive
  Lighter than Air
    Rises and Mixes with Air
Propane –
  Fossil fuel, Colorless, Odorless
    Odorant added for Identifiable Smell
  Non-toxic, Non-corrosive
  Heavier than Air
    Sinks, Pools, Stays In Excavation and will displace Oxygen

## Slide 3
Explosive Limits of Natural Gas
% GAS
100 % GAS
15 % GAS
5 % GAS
0 % GAS
TO RICH
TO LEAN
Flammable Range

## Slide 4
Explosive Limits of Propane Gas
% GAS
100 % GAS
10 % GAS
2 % GAS
0 % GAS
TO RICH
TO LEAN
Flammable Range

## Slide 5: Materials in Our System - Plastic - Mains And Services

## Slide 6: Materials in Our System - Cast Iron If you expose or undermine CI call and report it to the Gas Utility !
Cast Iron Pipe may need to be Supported if Exposed
Also, Depending on how much is Exposed or how large the Excavation is, the Cast Iron may need to be Replaced

## Slide 7: Materials in Our Systems – Wrought Iron And Bare and Coated Steel
Mains and Services
Many Old Pipes can be a “Sleeve Pipe” for Smaller Lines

## Slide 8
Abandoned 4” CS
2” PL Inserted into 4” CI
If markings are not Clear or were Missing, Causing Uncertainty … CALL the Utility Owner
DON’T TAKE CHANCES
Sleeved & Inserted Lines
The abandoned 4” CS appears to be in better condition than the CI, which has the LIVE 2” PL line inserted. The CI had holes in it but could not see Pipe inside. So, assumed the CS Pipe was the “Active” Pipe.

## Slide 9: Understanding Layout and Markings for Gas
Contractors are responsible for maintaining marks.
As illustrated here, services and mains are often not straight and have various depths depending on other items in the ground.
DigSafe marks are blind to depth.

## Slide 10: WATCH for Gas Line Markers !

## Slide 11: Recognize Signs of Gas in the Area Gas Meter Sets and Valves – Above Ground
Tracer Wire

## Slide 12: Recognize Signs of Gas Assets in the Distribution System - Below Ground
Notes: Some different tees, stubs, purge points, drips, etc.

## Slide 13: Recognize Signs of Gas Assets in the Distribution System - Below Ground: EXCESS FLOW VALVE
**DO NOT DO THIS**
Notes: Some different tees, stubs, purge points, drips, etc.

## Slide 14: Recognize the not so obvious Signs of Gas in the Area – REG STATIONS

## Slide 15: Recognize the not so obvious Signs of Gas in the Area – REG STATIONS
Verification of sense line locations
Verification of station critical valves
Required Tech Standby for Close Proximity
Location sense lines closer to facility or above ground
Temp Relocate of sense lines
Steel plating of assets outside facility

## Slide 16
Our Greatest Risk is Third Party Damage…
Site Work
Road Reconstruction
Replacing Utilities
Digging a Foundation
Placing Utility Poles
Routine Yard Work
Cross-Bore Damage
Notes: MOST FREQUENT CAUSES OF ACCIDENTS COME FROM
THIRD PARTY DAMAGES
THEY ARE:

## Slide 17: Cross Bore Examples & Damages

## Slide 18
  Stay Calm and Think – Do Not Attempt to Make Repairs
  Evacuate the area!
  CALL 911 from a Safe Location, Provide detailed description
  Call the Gas Company
  Protect the public, and prevent possible ignition sources
  Leave equipment and site as is – get to safety
  If gas has ignited, let it burn; do not attempt to put out the fire!
  DO NOT ATTEMPT TO REPAIR DAMAGE & DO NOT BACKFILL!
If You Damage / Rupture a Gas Line…

## Slide 19: Signs of a Ruptured Gas Line
  A blowing or hissing sound
  Dirt or Dust blowing from a hole
  Continuous bubbling in wet area
  A gaseous smell
  Flames, if gas has ignited
Notes: ACTION -
  Scratch and sniff the smell of gas
  You may hear gas if it is a high pressure line. Important to realize that you may not hear it.
  You may see “heat wave” like shimmer or dust. That could be gas escaping. Important to state again that this may not be evident.
  You will smell gas!

## Slide 20: Signs of Damage
Broken tracer wire or valve boxes
Coating Damages
Dents or Gouges
Report Damage – Do Not Backfill
Notes: Very important that you report all damages to us immediately.
The example here was found by one of our crews long after the damage had occurred. This was discovered while installing a gas service to a near by home. This facility is a 60 lbs main within 50 ft of residential structures; had this failed and leaked the scenario could have been catastrophic.
Report all types of minor of damages such as tape, coating, tracer wire…….. Use the Non-emergency # in your hand out to report minor occurrences.
Use the Emergency number to report major damages such as they example above immediately.

## Slide 21: Possible Ignition Sources
    Other Flames (pilot burner, match, cigarette lighters)
    Doorbells, Light Switches, Appliances
    Thermostats
    Cell Phones, 2-Way Radios
    Static Electricity
    Abrasive Saw or Grinders, Sparks
    And more!!
Notes: Ignition Temperature
Minimum Temperature Needed for a Mixture of Propane and Air to Ignite.
  The Ignition Temperature of Propane Is Between 920° F and 1,120° F
  A Common Ignition Source for Propane Is Another Flame, Such As the Flame of a Pilot Burner, Match or Cigarette Lighter.

## Slide 23: Questions / Comments
Thank you
FOR DIGGING SAFELY